WaterSim Pro

Models & Equations Reference

Comprehensive Technical Documentation

Version 16  |  February 2026

# 1. Introduction

WaterSim Pro is a process simulation platform for wastewater and water treatment plant design. It models each unit operation using established engineering equations — Monod kinetics for biological treatment, surface overflow rate correlations for clarifiers, Kozeny-Carman for filtration, and empirical models for chemical dosing, disinfection, and membrane separation.

This document provides a complete reference for every model and equation implemented in the simulation engine. Each chapter covers one unit operation with its governing equations, default parameters, assumptions, and output calculations.

## 1.1 Stream Properties

Every connection between unit operations carries a Stream object with the following water quality parameters:

| Parameter | Default Value | Unit |
| --- | --- | --- |
| Q | — | m³/d (volumetric flow rate) |
| TSS | — | mg/L (total suspended solids) |
| BOD | — | mg/L (5-day biochemical oxygen demand) |
| COD | — | mg/L (chemical oxygen demand) |
| TN | — | mg/L (total nitrogen) |
| NH₄ | — | mg/L (ammonia-nitrogen) |
| NO₃ | — | mg/L (nitrate-nitrogen) |
| NO₂ | — | mg/L (nitrite-nitrogen) |
| TP | — | mg/L (total phosphorus) |
| DO | — | mg/L (dissolved oxygen) |
| pH | — | dimensionless |
| temp | — | °C (temperature) |

## 1.2 Stream Mixing

When multiple streams merge at a node, concentrations are calculated as flow-weighted averages:

C_mix = Σ(C_i × Q_i) / Σ(Q_i)

This applies to all concentration parameters. Flow is simply summed: Q_mix = Σ(Q_i).

## 1.3 Solver Architecture

The solver performs a topological sort of the flowsheet graph, then propagates streams from inlet to outlet. For flowsheets with recycle loops (e.g., RAS from secondary clarifier to aeration basin), a fixed-point iteration is used:

- Maximum iterations: 50

- Convergence tolerance: ε = 0.0001 (relative change in Q, TSS, BOD, TN, NH₄, NO₃, TP)

- Converged when all tracked parameters change by less than ε between iterations

# 2. Inlet (Source)

The Inlet is a source node that defines the raw wastewater characteristics entering the treatment plant. It performs no transformation — the effluent equals the influent.

## 2.1 Default Influent Parameters

These represent typical medium-strength municipal wastewater:

| Parameter | Default Value | Unit |
| --- | --- | --- |
| Q | 10,000 | m³/d |
| TSS | 250 | mg/L |
| BOD | 200 | mg/L |
| COD | 400 | mg/L |
| TN | 45 | mg/L |
| NH₄ | 35 | mg/L |
| TP | 8 | mg/L |
| DO | 0 | mg/L |
| pH | 7.2 | — |
| temp | 20 | °C |

# 3. Screening

Screens remove large debris, rags, and coarse solids from the influent. The model applies empirical removal fractions based on screen type.

## 3.1 Removal Efficiencies by Screen Type

| Parameter | Default Value | Unit |
| --- | --- | --- |
| Coarse | TSS: 5%, BOD: 3%, COD: 3% | — |
| Fine | TSS: 15%, BOD: 10%, COD: 8% | — |
| Micro | TSS: 30%, BOD: 20%, COD: 15% | — |

## 3.2 Screenings Production

Screenings (kg/d) = Q (m³/d) × TSS_in (mg/L) × η_TSS / 1000

## 3.3 Effluent Calculation

TSS_eff = TSS_in × (1 - η_TSS)

BOD_eff = BOD_in × (1 - η_BOD)

COD_eff = COD_in × (1 - η_COD)

All other parameters (TN, NH₄, NO₃, TP, DO, pH, temp) pass through unchanged. Q is unchanged.

# 4. Grit Removal

Grit chambers remove heavy inorganic particles (sand, gravel, cinders) that could damage downstream equipment. The model is based on chamber type and hydraulic retention time.

## 4.1 Removal Efficiencies by Chamber Type

| Parameter | Default Value | Unit |
| --- | --- | --- |
| Horizontal | TSS: 10%, BOD: 2%, COD: 2% | — |
| Aerated | TSS: 15%, BOD: 3%, COD: 3% | — |
| Vortex | TSS: 12%, BOD: 2%, COD: 2% | — |

## 4.2 Chamber Sizing

Q_m3_min = Q (m³/d) / 1440

Volume (m³) = Q_m3_min × HRT_min

## 4.3 Grit Production

Grit (kg/d) = Q (m³/d) × TSS_in (mg/L) × η_TSS / 1000

# 5. Primary Clarifier

Primary clarifiers remove settleable solids by gravity sedimentation. The model uses Surface Overflow Rate (SOR) to predict TSS removal, with BOD and COD removal derived proportionally.

## 5.1 Default Parameters

| Parameter | Default Value | Unit |
| --- | --- | --- |
| SOR | 40 | m³/m²/d |
| Depth | 3.5 | m |
| Sludge TSS | 25,000 | mg/L (2.5% DS) |

## 5.2 Sizing Equations

Area (m²) = Q / SOR

Volume (m³) = Area × depth

HRT (h) = (Volume / Q) × 24

## 5.3 TSS Removal (empirical hyperbolic)

The TSS removal efficiency is a function of SOR, following a hyperbolic relationship:

η_TSS = min(0.70, max(0.30, 65 / (40 + SOR) + 0.25))

This yields ~55% removal at SOR = 40 m³/m²/d, decreasing as overflow rate increases.

## 5.4 BOD and COD Removal

η_BOD = η_TSS × 0.55

η_COD = η_BOD × 0.90

## 5.5 Mass Balance and Sludge Flow

TSS_removed (kg/d) = Q × TSS_in × η_TSS / 1000

Sludge_Q (m³/d) = TSS_removed (kg/d) / (sludge_TSS / 1000)

Effluent_Q = Q_in - Sludge_Q

## 5.6 Effluent Quality

TSS_eff = TSS_in × (1 - η_TSS) × Q_in / Q_eff

BOD_eff = BOD_in × (1 - η_BOD)

COD_eff = COD_in × (1 - η_COD)

TN_eff = TN_in × 0.98  (minor removal)

TP_eff = TP_in × 0.95  (minor removal)

# 6. Activated Sludge (Aeration Basin)

The aeration basin is the core biological treatment unit. It models carbonaceous BOD removal, nitrification, denitrification, and optional Enhanced Biological Phosphorus Removal (EBPR) using Monod kinetics.

## 6.1 Default Kinetic Parameters

| Parameter | Default Value | Unit |
| --- | --- | --- |
| SRT | 10 | days (solids retention time) |
| DO setpoint | 2.0 | mg/L |
| MLSS | 3,000 | mg/L |
| Y (yield) | 0.60 | g VSS/g BOD |
| k_d (decay) | 0.06 | 1/d |
| μ_max,BOD | 6.0 | 1/d (at 20°C) |
| K_s,BOD | 60 | mg/L |
| μ_max,NH4 | 0.75 | 1/d (nitrifiers) |
| K_s,NH4 | 0.74 | mg/L |
| K_s,DO | 0.2 | mg/L |
| θ (temp coeff) | 1.07 | — |
| μ_max,denit | 0.40 | 1/d |
| K_s,NO3 | 0.10 | mg/L |
| BOD:N ratio | 3.5 | mg BOD/mg N for denitrification |

## 6.2 Temperature Correction

All maximum growth rates are corrected for temperature using the Arrhenius-type equation:

μ(T) = μ(20°C) × θ^(T - 20)

Where θ = 1.07 (default). At 15°C the rate drops to ~71% of the 20°C value; at 25°C it rises to ~140%.

## 6.3 BOD Removal (Monod Kinetics)

The effluent BOD is determined by the minimum substrate concentration that sustains biomass at the given SRT:

BOD_eff = K_s,BOD × (1 + k_d × SRT) / (SRT × (Y × μ_max,BOD - k_d) - 1)

This is the classic Lawrence-McCarty equation. Lower SRT gives higher effluent BOD; longer SRT gives better removal but more oxygen demand.

## 6.4 Nitrification (Ammonia Oxidation)

Nitrification occurs when the SRT exceeds the minimum SRT for nitrifier growth:

SRT_min,nit = 1 / μ_max,NH4

If SRT > 1.5 × SRT_min,nit (full nitrification):

NH4_eff = K_s,NH4 × (1 + k_d × SRT) / (SRT × (μ_max,NH4 - k_d) - 1)

Otherwise, partial nitrification efficiency is:

efficiency = SRT / (1.5 × SRT_min,nit)

NH4_eff = NH4_in × (1 - efficiency × 0.90)

NH4_nitrified = NH4_in - NH4_eff

NO3_produced = NO3_in + NH4_nitrified

## 6.5 Denitrification (Anoxic Zone)

Denitrification reduces nitrate to nitrogen gas using BOD as the carbon source:

max_NO3_removable = BOD_in / BOD_NO3_ratio

kinetic_floor = max(0, K_s,NO3 × (1 + k_d×SRT) / (SRT×(μ_denit - k_d) - 1))

NO3_eff = max(kinetic_floor, NO3_produced - max_NO3_removable)

The BOD consumed by denitrification:

BOD_consumed_denit = (NO3_produced - NO3_eff) × BOD_NO3_ratio

## 6.6 Oxygen Demand

The total oxygen demand integrates carbonaceous oxidation, endogenous respiration, and nitrification:

O2 (kg/d) = Q/1000 × (1.5 × BOD_removed - 1.42 × biomass_prod + 4.33 × NH4_nitrified)

Where:

- 1.5 = oxygen factor for BOD oxidation

- 1.42 = oxygen equivalent of cell mass (COD of VSS)

- 4.33 = oxygen for nitrification (NH₄-N → NO₃-N)

## 6.7 Biomass Production

P_x (kg/d) = Q × BOD_removed × Y / ((1 + k_d × SRT) × 1000)

## 6.8 Volume Sizing

MLVSS = MLSS × 0.80

Volume (m³) = max(50, P_x (kg/d) × 1000 × SRT / MLVSS)

HRT (h) = (Volume / Q) × 24

## 6.9 WAS Flow

WAS_Q (m³/d) = P_x (kg/d) × 1000 / MLSS

## 6.10 EBPR — Enhanced Biological Phosphorus Removal

Three EBPR configurations are supported:

### 6.10.1 Simple EBPR

VFA_available = COD_in × VFA_COD_fraction

P_released = VFA_available × 0.5

P_uptake = P_released × ebpr_uptake_rate × Y_PAO × PAO_fraction

### 6.10.2 UCT Configuration (University of Cape Town)

Process train: RAS → Anoxic → Anaerobic → Aerobic

Key principle: No nitrate recycle to the anaerobic zone. Mixed Liquor Recycle (MLR) removes NO₃ in the anoxic zone before flow enters the anaerobic zone.

Q_MLR (m³/d) = Q_in × MLR_ratio

NO3_suppress = max(0.2, 1 - (NO3_to_anaerobic - 1) / 20)  if NO3 > 1

### 6.10.3 JHB Configuration (Johannesburg)

Process train: Influent → Pre-anoxic (with RAS) → Anaerobic → Main Anoxic → Aerobic

The pre-anoxic zone denitrifies the RAS stream before it enters the anaerobic zone:

preanox_BOD = BOD_in × jhb_preanoxic_fraction × 5

# 7. Secondary Clarifier

The secondary clarifier separates activated sludge biomass from the treated effluent using gravity settling. It produces a clarified effluent and a concentrated Return Activated Sludge (RAS) stream.

## 7.1 Default Parameters

| Parameter | Default Value | Unit |
| --- | --- | --- |
| SOR | 16 | m³/m²/d |
| Depth | 4.0 | m |
| RAS ratio | 0.5 | — |
| RAS TSS | 8,000 | mg/L |
| Effluent TSS | 12 | mg/L |

## 7.2 Sizing

Area (m²) = Q_in / SOR

Volume (m³) = Area × depth

HRT (h) = (Volume / Q_in) × 24

## 7.3 Solids Balance

RAS_Q (m³/d) = Q_in × RAS_ratio

Effluent_Q = Q_in - RAS_Q

Solids_in (kg/d) = Q_in × MLSS / 1000

Solids_eff (kg/d) = Effluent_Q × TSS_eff / 1000

Solids_RAS (kg/d) = Solids_in - Solids_eff

RAS_TSS (mg/L) = Solids_RAS × 1000 / RAS_Q

## 7.4 Solids Loading Rate

SLR (kg TSS/m²/d) = Solids_in / Area

Warning issued if SLR exceeds 6.0 kg/m²/d (risk of solids blanket overflow).

# 8. Anaerobic Digester (ADM1-lite)

The anaerobic digester model is a steady-state simplification of the IWA Anaerobic Digestion Model No. 1 (ADM1). It models the four-stage biochemical pathway: hydrolysis, acidogenesis, acetogenesis, and methanogenesis.

## 8.1 Default Parameters

| Parameter | Default Value | Unit |
| --- | --- | --- |
| HRT | 20 | days |
| Temperature | 35 | °C (mesophilic) |
| COD removal target | 55 | % |
| k_hyd | 0.3 | 1/d (hydrolysis rate at 35°C) |
| pH setpoint | 7.2 | — |
| VS:COD ratio | 1.42 | g COD/g VS |
| Biogas CH₄ fraction | 0.65 | — |
| Dewatering | false | — |
| Cake DS | 22 | % |

## 8.2 Temperature Correction

Mesophilic (25–45°C): k_corr = 1.08^(T - 35)

Thermophilic (45–60°C): k_corr = 1.7 × 1.06^(T - 55)

Below 15°C: k_corr = 0.15 (severe inhibition)

## 8.3 COD Destruction

k_eff = k_hyd × k_corr(T)

kinetic_fraction = 1 - exp(-k_eff × HRT)

COD_destruction = min(kinetic_fraction, target_removal)

## 8.4 Biogas Production

80% of influent COD is assumed particulate/colloidal:

COD_hydrolysed = COD_in × 0.80 × COD_destruction

VFA_formed = COD_hydrolysed × 0.85

COD_to_CH4 = VFA_formed × 0.70

Methane yield (stoichiometric):

CH4 (m³/d) = COD_to_CH4 (kg/d) × 0.35  [0.35 m³ CH4 STP per kg COD]

Biogas (m³/d) = CH4 / CH4_fraction

## 8.5 Energy Recovery

Energy (kWh/d) = CH4 (m³/d) × 10 × 0.35

Where 10 kWh/m³ is the higher heating value of methane and 0.35 is the CHP generator efficiency.

## 8.6 Digestate Quality

VS_destruction = COD_destruction × 0.90

VSS_out = VSS_in × (1 - VS_destruction)

TSS_out = VSS_out + ISS_in  [ISS = inert fraction = 25% of feed TSS]

Nitrogen release (ammonification):

org_N_in = (TN_in - NH4_in) × 0.9

NH4_released = org_N_in × COD_destruction × 0.70

NH4_out = NH4_in + NH4_released

## 8.7 Stability Criteria

- VFA/Alkalinity ratio < 0.3 for stable operation

- pH ≥ 6.8 to avoid methanogenic inhibition

- HRT ≥ 15 days recommended; < 10 days risks washout

- Temperature 30–40°C (mesophilic) or 50–60°C (thermophilic)

# 9. UV Disinfection

UV disinfection inactivates pathogens using ultraviolet radiation at 254 nm. The model uses the UV fluence (dose) approach based on organism-specific inactivation constants.

## 9.1 Default Parameters

| Parameter | Default Value | Unit |
| --- | --- | --- |
| Target log reduction | 4 | log₁₀ |
| UVT | 65 | % (UV transmittance at 254 nm) |
| Lamp power | 0.4 | kW per lamp |
| Lamp capacity | 50 | m³/h per lamp bank |
| k_inact (E. coli) | 19 | mJ/cm² |

## 9.2 Inactivation Constants (k_inact)

| Parameter | Default Value | Unit |
| --- | --- | --- |
| E. coli | 19 | mJ/cm² |
| Total coliforms | 21 | mJ/cm² |
| Cryptosporidium | 10 | mJ/cm² (UV-sensitive) |
| Giardia | 82 | mJ/cm² |
| Adenovirus | 186 | mJ/cm² (UV-resistant) |

## 9.3 UV Fluence (Dose) Calculation

Required fluence = target_log_reduction × k_inact

UVT correction = √(UVT / 65)   [normalized to 65% reference]

Fluence_delivered = Required_fluence × UVT_correction

## 9.4 Lamp Sizing

Lamp count = ⌈ Q (m³/h) / lamp_capacity ⌉

Energy (kWh/d) = lamp_count × lamp_power × 24

## 9.5 Log Reduction Achieved

Log reduction = Fluence_delivered / k_inact

Compliance check: target achieved if log deficit < 0.05.

# 10. Granular Media Filter

The granular filter model uses Kozeny-Carman head loss equations and empirical breakthrough curves to predict filtration performance for dual-media or sand filters.

## 10.1 Default Parameters

| Parameter | Default Value | Unit |
| --- | --- | --- |
| Filter type | dual_media | — |
| HLR | 8 | m/h (hydraulic loading rate) |
| TSS removal | 90 | % |
| Backwash interval | 24 | hours |
| Head loss limit | 2.5 | m |
| Sand depth | 0.30 | m |
| Sand d₅₀ | 0.5 | mm |
| Anthracite depth | 0.45 | m (dual-media only) |
| Anthracite d₅₀ | 1.4 | mm |

## 10.2 Kinematic Viscosity

ν(T) = 10⁻⁶ / (1 + 0.0337×T + 0.000221×T²)  [m²/s]

## 10.3 Kozeny-Carman Clean-Bed Head Loss

For each media layer (anthracite, sand):

f_K = 180 × (1-ε)² / ε³   [Kozeny constant]

h_L = (f_K × ν × v × L) / (g × d_e²)

Where ε = porosity, v = filtration velocity (m/s), L = bed depth (m), g = 9.81 m/s², d_e = effective grain diameter (m).

h_clean = h_anthracite + h_sand

## 10.4 Clogging Model

TSS_load (kg/m²) = (TSS_in/1000) × Q_m3_h × t_backwash / Area

h_clogged = h_clean + 0.4 × TSS_load  [0.4 m per kg/m²]

Backwash triggered when h_clogged > h_limit (default 2.5 m).

## 10.5 TSS Breakthrough

TSS_capacity = 0.8 × (1.4 for dual-media, 1.0 for sand)

Breakthrough = min(1, TSS_load / TSS_capacity)

Effective removal = target × (1 - 0.15 × Breakthrough)

## 10.6 Filtrate Quality

TSS_filtrate = TSS_in × (1 - effective_removal)

BOD_filtrate = BOD_in × (1 - effective_removal × 0.45)

COD_filtrate = COD_in × (1 - effective_removal × 0.30)

Q_backwash = Q_in × 0.05  [5% consumption]

# 11. Reverse Osmosis Membrane

The RO model simulates pressure-driven membrane separation, splitting the feed into high-quality permeate and a concentrated reject stream.

## 11.1 Default Parameters

| Parameter | Default Value | Unit |
| --- | --- | --- |
| Recovery | 75 | % |
| Salt rejection | 0.97 | — |
| TN rejection | 0.85 | — |
| TP rejection | 0.98 | — |
| BOD rejection | 0.99 | — |
| TSS rejection | 1.00 | — |
| Operating pressure | 15 | bar |

## 11.2 Flow Split

Permeate_Q = Q_in × Recovery

Concentrate_Q = Q_in × (1 - Recovery)

Concentration_Factor = 1 / (1 - Recovery)

## 11.3 Permeate Quality

TSS_perm = 0  [complete removal]

BOD_perm = BOD_in × (1 - BOD_rejection)

TN_perm = TN_in × (1 - TN_rejection)

TP_perm = TP_in × (1 - TP_rejection)

## 11.4 Concentrate Quality

C_concentrate = C_in × CF × rejection

Each parameter is concentrated by the concentration factor and rejection coefficient.

## 11.5 Energy Consumption

Energy (kWh/d) = Permeate_Q × (pressure / 15) × 0.5

Where 0.5 kWh/m³ is the reference specific energy at 15 bar.

# 12. Chemical Dosing

The chemical dosing model handles coagulation (phosphorus removal), pH adjustment, and disinfection based on chemical type and dose.

## 12.1 Chemical Coefficients

| Parameter | Default Value | Unit |
| --- | --- | --- |
| Alum — TP removal | 0.23 | mg TP per mg alum |
| Alum — TSS increase | 0.26 | mg TSS per mg alum (Al(OH)₃ floc) |
| FeCl₃ — TP removal | 0.17 | mg TP per mg FeCl₃ |
| FeCl₃ — TSS increase | 0.40 | mg TSS per mg FeCl₃ (Fe(OH)₃ floc) |
| NaOH — pH change | +0.01 | pH per mg/L NaOH |
| H₂SO₄ — pH change | -0.008 | pH per mg/L H₂SO₄ |
| NaOCl — BOD removal | 8% | fraction |
| NaOCl — TSS removal | 2% | fraction |

## 12.2 Coagulant Dose Calculation

Dose (kg/d) = Q (m³/d) × dose (mg/L) / 1000

TP_removed = min(TP_in, dose × TP_removal_coeff)

TP_eff = max(0, TP_in - TP_removed)

TSS_eff = TSS_in + dose × TSS_increase_coeff

## 12.3 pH Adjustment

If target_pH set: pH_eff = target_pH

Otherwise: pH_eff = clamp(pH_in + dose × pH_change_coeff, 0, 14)

# 13. Cost Estimation Model

The cost estimator calculates annual operating costs across five categories based on simulation results and configurable unit cost parameters.

## 13.1 Default Unit Costs

| Parameter | Default Value | Unit |
| --- | --- | --- |
| Electricity | 0.12 | $/kWh |
| Aeration energy | 1.0 | kWh/kg O₂ transferred |
| Pumping | 0.04 | kWh/m³ |
| Coagulant (alum) | 0.30 | $/kg |
| Polymer | 3.50 | $/kg |
| Disinfectant (NaOCl) | 0.25 | $/kg |
| Biosolids disposal | 80 | $/tonne (dry) |
| Operator salary | 60,000 | $/year |
| Maintenance | 2% | of CapEx/year |
| CapEx factor | 1,200 | $/m³·d capacity |

## 13.2 Energy Cost

Aeration (kWh/d) = Σ(O2_demand) × aeration_kWh_per_kgO2

Pumping (kWh/d) = Q × pumping_kWh_per_m3

Energy cost ($/yr) = (Aeration + Pumping) × 365 × electricity_rate

## 13.3 Chemical Costs

Coagulant ($/yr) = Q × dose/1000 × 365 × unit_cost

Polymer ($/yr) = WAS_Q × dose/1000 × 365 × unit_cost

Disinfectant ($/yr) = Q × dose/1000 × 365 × unit_cost

## 13.4 Sludge Disposal

Dry solids (t/yr) = Σ(biomass_kg_d) / 1000 × 365

Disposal cost ($/yr) = dry_tonnes/yr × biosolids_rate

## 13.5 Labour

Staff count = max(2, round(Q_MLD / 5))

Labour cost ($/yr) = Staff × salary

## 13.6 Maintenance

CapEx estimate ($) = Q (m³/d) × 1,200 $/m³·d

Maintenance ($/yr) = CapEx × 2%

## 13.7 Total Annual Cost

Total ($/yr) = Energy + Chemicals + Sludge + Labour + Maintenance

Unit cost ($/m³) = Total / (Q × 365)

# 14. Dynamic Simulation (Diurnal Profile)

The dynamic solver wraps the steady-state engine in a time-step loop. At each hourly step, inlet parameters are scaled by diurnal multipliers to simulate 24-hour flow variation.

## 14.1 Scaling Equation

Parameter(h) = Base_value × Scale_factor(h)

Applied to: Q, BOD, TN, TP, TSS, and NH₄ (NH₄ scales with TN).

Not scaled: COD, pH, temperature, DO.

## 14.2 Default Diurnal Profile

The default profile represents a typical municipal wastewater pattern:

| Parameter | Default Value | Unit |
| --- | --- | --- |
| 00:00–05:00 | 0.50–0.60 | Night low (minimum at 3 AM) |
| 06:00–08:00 | 0.80–1.30 | Morning rise |
| 09:00–12:00 | 1.40–1.50 | Morning peak (max at 11 AM) |
| 13:00–16:00 | 1.20–1.35 | Afternoon moderate |
| 17:00–19:00 | 1.25–1.30 | Evening peak |
| 20:00–23:00 | 0.68–1.10 | Night decline |

## 14.3 Constant Inlet Mode

When the "Constant Inlet" option is enabled, all scale factors are set to 1.0, and inlet parameters remain at their base values throughout the simulation.

# 15. Outlet (Discharge Compliance)

The outlet node performs no treatment. It checks effluent quality against discharge permit limits and flags violations.

## 15.1 Default Permit Limits

| Parameter | Default Value | Unit |
| --- | --- | --- |
| BOD | 30 | mg/L |
| TSS | 30 | mg/L |
| TN | 10 | mg/L |
| TP | 1 | mg/L |
| NH₄ | 5 | mg/L |
| pH range | 6.0–9.0 | — |